## TB_IO
Terminal Board Quantity: |  | 2 |  | Quote #: | 1523_R5 | 1
|  |  |  | SAP #: | 1014-1577-00 | 2
|  |  |  | DWG #: | 650-5900-88-15-14 | 3
4
CONTROL BOARD OUTPUTS | [5 empty] | 5
OUTPUT # | OUTPUT NAME / FUNCTION |  |  |  | DEVICE TAG
DS1 | Fuel |  |  |  | N/A
DS2 | Ignition |  |  |  | N/A
DS3 | Start Crank |  |  |  | N/A
DS4 | Auxiliary Lube |  |  |  | N/A
TERMINAL BOARD 1 I/O
INPUT # | INPUT NAME / FUNCTION |  | SWITCH CONFIGURATION |  | DEVICE TAG
IN1 | Suction Stage 1 Pressure |  | 4-20mA |  |  | 4-20mA
IN2 | Discharge Stage 1 Pressure |  | 4-20mA |  |  | 0-5VDC (ANALOG)
IN3 |  |  | NOT USED |  |  | J/K T/C
IN4 | Discharge Stage 2 Pressure |  | 4-20mA |  |  | N/C DI
IN5 | 3rd Stage Suction Pressure |  | 4-20mA |  |  | N/O DI
IN6 | 3rd Stage Discharge Pressure |  | 4-20mA |  |  | NOT USED
IN7 | Compressor Lube Oil Pressure |  | 4-20mA
IN8 | Engine Lube Oil Pressure |  | 4-20mA
IN9 | GD01 Gas Detector- Comp side |  | 4-20mA
IN10 | GD012 Gas Detector- Engine side |  | 4-20mA
IN11 |  |  | NOT USED
IN12 |  |  | NOT USED
IN13 |  |  | NOT USED
IN14 |  |  | NOT USED
IN15 |  |  | NOT USED
IN16 |  |  | NOT USED
IN17 | Lube No Flow switch |  | N/C DI
IN18 | Engine Oil Level LSLL |  | N/C DI
IN19 | Compressor Oil Level LSLL |  | N/C DI
IN20 | Engine JW water Level LSLL |  | N/C DI
IN21 | Engine Aux Water Level LSLL |  | N/C DI
IN22 | Cooler Vibration VSHH |  | N/C DI
IN23 | Compressor Vibration VSHH |  | N/C DI
IN24 | Engine Vibration VSHH |  | N/C DI
IN25 | 1st STG Scrubber Level HIGH |  | N/C DI
IN26 | 2nd Stg Scrubber Level HIGH |  | N/C DI
IN27 | 3rd STG Scrubber Level HIGH |  | N/C DI
IN28 | CEC DSM Fault |  | N/C DI
IN29 | Engine Started |  | N/C DI
IN30 | Remote Stop USD |  | N/C DI
IN31 | Station ESD |  | N/C DI
IN32 | Panel Emergency Stop |  | N/C DI
OUTPUT # | OUTPUT NAME / FUNCTION |  |  |  | DEVICE TAG
AO1 | Suction Control Out
AO2 | Engine Speed Control Out
AO3 | Recycle Valve Control Out
AO4
DO1 | Fuel Valve
DO2 | Not Used
DO3 | Bypass Valve Open
DO4 | Blowdown Valve Close
DO5 | RUN STATUS
DO6 | ALARM HORN
DO7 | ALARM STATUS
DO8 | FAULT STATUS
RPM1 | Engine RPM
RPM2
TERMINAL BOARD 2 I/O
INPUT # | INPUT NAME / FUNCTION |  | SWITCH CONFIGURATION |  | DEVICE TAG
IN1 | COMPRESSOR OIL TEMP |  | J/K T/C
IN2 | CYL#1 DISCHARGE TEMP |  | J/K T/C
IN3 | CYL#2 DISCHARGE TEMP |  | J/K T/C
IN4 | CYL#3 DISCHARGE TEMP |  | J/K T/C
IN5 | CYL#4 DISCHARGE TEMP |  | J/K T/C
IN6 |  |  | NOT USED
IN7 |  |  | NOT USED
IN8 |  |  | NOT USED
IN9 | ENGINE OIL TEMP |  | J/K T/C
IN10 | ENGINE JACKET WATER TEMP |  | J/K T/C
IN11 | Engine ESD Right Side |  | N/C DI
IN12 | Engine ESD Left Side |  | N/C DI
IN13 |  |  | NOT USED
IN14 |  |  | NOT USED
IN15 |  |  | NOT USED
IN16 |  |  | NOT USED
IN17 | ENGINE EXHAUST CYL 1 Left |  | J/K T/C
IN18 | ENGINE EXHAUST CYL 2 Left |  | J/K T/C
IN19 | ENGINE EXHAUST CYL 3 Left |  | J/K T/C
IN20 | ENGINE EXHAUST CYL 4 Left |  | J/K T/C
IN21 | ENGINE EXHAUST CYL 5 Left |  | J/K T/C
IN22 | ENGINE EXHAUST CYL 6 Left |  | J/K T/C
IN23 | ENGINE EXHAUST CYL 1 Right |  | J/K T/C
IN24 | ENGINE EXHAUST CYL 2 Right |  | J/K T/C
IN25 | ENGINE EXHAUST CYL 3 Right |  | J/K T/C
IN26 | ENGINE EXHAUST CYL 4 Right |  | J/K T/C
IN27 | ENGINE EXHAUST CYL 5 Right |  | J/K T/C
IN28 | ENGINE EXHAUST CYL 6 Right |  | J/K T/C
IN29 | ENGINE EXHAUST PRE TURBO Left |  | J/K T/C
IN30 | ENGINE EXHAUST PRE TURBO Right |  | J/K T/C
IN31 | ENGINE AIR MANIFOLD Left |  | J/K T/C
IN32 | ENGINE AIR MANIFOLD Right |  | J/K T/C
OUTPUT # | OUTPUT NAME / FUNCTION |  |  |  | DEVICE TAG
AO1
AO2
AO3
AO4
DO1
DO2
DO3
DO4 | ENGINE PRE LUBE
DO5 | STROBE LIGHT RUNNING GREEN
DO6 | STROBE LIGHT ALARM AMBER
DO7 | STROBE LIGHT FAULT RED
DO8 | STROBE LIGHT FLASH
RPM1
RPM2
TERMINAL BOARD 3 I/O
INPUT # | INPUT NAME / FUNCTION |  | SWITCH CONFIGURATION |  | DEVICE TAG
IN1 |  |  | NOT USED
IN2 |  |  | NOT USED
IN3 |  |  | NOT USED
IN4 | SUCTION PRESSURE SWITCH LOW |  | N/C DI
IN5 | STG 1DISCHARGE PRESSURE SWITCH HIGH |  | N/C DI
IN6 | STG 2 DISCHARGE PRESSURE SWITCH HIGH |  | N/C DI
IN7 | COMPRESSOR LUBE OIL PRESSURE LOW SWITCH |  | N/C DI
IN8 | CYLINDER LUBE PRESSURE LOW SWITCH |  | N/C DI
IN9 | ENGINE JACKET WATER FLOW SWITCH |  | N/C DI
IN10 | SPARE |  | N/C DI
IN11 | ENGINE LUBE OIL LEVEL LOW SWITCH |  | N/C DI
IN12 | COMP LUBE OIL LEVEL LOW SWITCH |  | N/C DI
IN13 | STG 1 SCRUBBER LEVEL HIGH SWITCH |  | N/C DI
IN14 | STG2 SCRUBBER LEVEL HIGH SWITCH |  | N/C DI
IN15 | SPARE |  | N/C DI
IN16 | SPARE |  | N/C DI
IN17 | LUBE NO FLOW CPI FSLL |  | N/C DI
IN18 | SPARE |  | N/C DI
IN19 | SPARE |  | N/C DI
IN20 | IGNITION FAULT |  | N/C DI
IN21 | COMPRESSOR CYLINDER VIBRATION #1 |  | N/C DI
IN22 | COMPRESSOR CYLINDER VIBRATION #2 |  | N/C DI
IN23 | COMPRESSOR COOLER VIBRATION #1 |  | N/C DI
IN24 | COMPRESSOR COOLER VIBRATION#2 |  | N/C DI
IN25 | SPARE |  | N/C DI
IN26 | SPARE |  | N/C DI
IN27 | SPARE |  | N/C DI
IN28 | SPARE |  | N/C DI
IN29 | SPARE |  | N/C DI
IN30 | SPARE |  | N/C DI
IN31 | REMOTE ESD |  | N/C DI
IN32 | PANEL EMERGENCY STOP |  | N/C DI
OUTPUT # | OUTPUT NAME / FUNCTION |  |  |  | DEVICE TAG
AO1
AO2
AO3
AO4
DO1
DO2
DO3
DO4
DO5
DO6
DO7
DO8
RPM1
RPM2
TERMINAL BOARD 4 I/O
INPUT # | INPUT NAME / FUNCTION |  | SWITCH CONFIGURATION |  | DEVICE TAG
IN1 | Pre-Turbo Flywheel Exhaust Temp |  | J/K T/C
IN2 | Post Turbo Flywheel Exhaust Temp |  | J/K T/C
IN3 | Pre-Turbo Aux End Exhaust Temp |  | J/K T/C
IN4 | Post Turbo Aux End Exhaust Temp |  | J/K T/C
IN5 | Engine Bearing 1 Temp |  | J/K T/C
IN6 | Engine Bearing 2 Temp |  | J/K T/C
IN7 | Engine Bearing 3 Temp |  | J/K T/C
IN8 | Engine Bearing 4 Temp |  | J/K T/C
IN9 | Engine Bearing 5 Temp |  | J/K T/C
IN10 | Engine Bearing 6 Temp |  | J/K T/C
IN11 | Engine Bearing 7 Temp |  | J/K T/C
IN12 | Engine Bearing 8 Temp |  | J/K T/C
IN13 | Engine Bearing 9 Temp |  | J/K T/C
IN14 |  |  | NOT USED
IN15 |  |  | NOT USED
IN16 |  |  | NOT USED
IN17 |  |  | NOT USED
IN18 |  |  | NOT USED
IN19 |  |  | NOT USED
IN20 |  |  | NOT USED
IN21 |  |  | NOT USED
IN22 |  |  | NOT USED
IN23 |  |  | NOT USED
IN24 |  |  | NOT USED
IN25 |  |  | NOT USED
IN26 |  |  | NOT USED
IN27 |  |  | NOT USED
IN28 |  |  | NOT USED
IN29 |  |  | NOT USED
IN30 |  |  | NOT USED
IN31 |  |  | NOT USED
IN32 |  |  | NOT USED
OUTPUT # | OUTPUT NAME / FUNCTION |  |  |  | DEVICE TAG
AO1
AO2
AO3
AO4
DO1
DO2
DO3
DO4
DO5
DO6
DO7
DO8
RPM1
RPM2
TERMINAL BOARD 5 I/O
INPUT # | INPUT NAME / FUNCTION |  | SWITCH CONFIGURATION |  | DEVICE TAG
IN1 |  |  | NOT USED
IN2 |  |  | NOT USED
IN3 |  |  | NOT USED
IN4 |  |  | NOT USED
IN5 |  |  | NOT USED
IN6 |  |  | NOT USED
IN7 |  |  | NOT USED
IN8 |  |  | NOT USED
IN9 |  |  | NOT USED
IN10 |  |  | NOT USED
IN11 |  |  | NOT USED
IN12 |  |  | NOT USED
IN13 |  |  | NOT USED
IN14 |  |  | NOT USED
IN15 |  |  | NOT USED
IN16 |  |  | NOT USED
IN17 |  |  | NOT USED
IN18 |  |  | NOT USED
IN19 |  |  | NOT USED
IN20 |  |  | NOT USED
IN21 |  |  | NOT USED
IN22 |  |  | NOT USED
IN23 |  |  | NOT USED
IN24 |  |  | NOT USED
IN25 |  |  | NOT USED
IN26 |  |  | NOT USED
IN27 |  |  | NOT USED
IN28 |  |  | NOT USED
IN29 |  |  | NOT USED
IN30 |  |  | NOT USED
IN31 |  |  | NOT USED
IN32 |  |  | NOT USED
OUTPUT # | OUTPUT NAME / FUNCTION |  |  |  | DEVICE TAG
AO1
AO2
AO3
AO4
DO1
DO2
DO3
DO4
DO5
DO6
DO7
DO8
RPM1
RPM2

## 16 bit registers
DE-4000 MODBUS REGISTER MAPPING (16 bit registers available at the configured node # in the HMI)
ADDRESS | DESCRIPTION | BIT | FUNCTION | DEVICE TAG
40001 | ENGINE STATE | 0 | READY TO START
|  | 1 | WARNING
|  | 2 | PRE-LUBE
|  | 3 | CRANK
|  | 4 | IGNITION
|  | 5 | FUEL
|  | 6 | CRANK DISCONNECT
|  | 7 | WARMUP
|  | 8 | RUNNING
|  | 9 | COOLDOWN
10
40002 | Hourmeter # of Hours - (Unsigned 0-65535)
40003 | Hourmeter # of Minutes - (0-59)
40004 | STATUS FAULT Terminal Module T1 Channel Fault = 1-32 Terminal Module T2 Channel Fault = 33-64 Terminal Module T3 Channel Fault = 65-96 Terminal Module T4 Channel Fault = 97-128 Terminal Module T5 Channel Fault = 129 - 160 Speed Channel fault = 161-170 (T1:SP1, T1:SP2, T2:SP1, T2:SP2, etc.) Overcrank = 171 Stop = 0 Timers Active = 254 Running = 255 | 0 | STOP
|  | 1 | Suction Stage 1 Pressure
|  | 2 | Discharge Stage 1 Pressure
3
|  | 4 | Discharge Stage 2 Pressure
|  | 5 | 3rd Stage Suction Pressure
|  | 6 | 3rd Stage Discharge Pressure
|  | 7 | Compressor Lube Oil Pressure
|  | 8 | Engine Lube Oil Pressure
|  | 9 | GD01 Gas Detector- Comp side
|  | 10 | GD012 Gas Detector- Engine side
11
12
13
14
15
16
|  | 17 | Lube No Flow switch
|  | 18 | Engine Oil Level LSLL
|  | 19 | Compressor Oil Level LSLL
|  | 20 | Engine JW water Level LSLL
|  | 21 | Engine Aux Water Level LSLL
|  | 22 | Cooler Vibration VSHH
|  | 23 | Compressor Vibration VSHH
|  | 24 | Engine Vibration VSHH
|  | 25 | 1st STG Scrubber Level HIGH
|  | 26 | 2nd Stg Scrubber Level HIGH
|  | 27 | 3rd STG Scrubber Level HIGH
|  | 28 | CEC DSM Fault
|  | 29 | Engine Started
|  | 30 | Remote Stop USD
|  | 31 | Station ESD
|  | 32 | Panel Emergency Stop
|  | 33 | COMPRESSOR OIL TEMP
|  | 34 | CYL#1 DISCHARGE TEMP
|  | 35 | CYL#2 DISCHARGE TEMP
|  | 36 | CYL#3 DISCHARGE TEMP
|  | 37 | CYL#4 DISCHARGE TEMP
38
39
40
|  | 41 | ENGINE OIL TEMP
|  | 42 | ENGINE JACKET WATER TEMP
|  | 43 | Engine ESD Right Side
|  | 44 | Engine ESD Left Side
45
46
47
48
|  | 49 | ENGINE EXHAUST CYL 1 Left
|  | 50 | ENGINE EXHAUST CYL 2 Left
|  | 51 | ENGINE EXHAUST CYL 3 Left
|  | 52 | ENGINE EXHAUST CYL 4 Left
|  | 53 | ENGINE EXHAUST CYL 5 Left
|  | 54 | ENGINE EXHAUST CYL 6 Left
|  | 55 | ENGINE EXHAUST CYL 1 Right
|  | 56 | ENGINE EXHAUST CYL 2 Right
|  | 57 | ENGINE EXHAUST CYL 3 Right
|  | 58 | ENGINE EXHAUST CYL 4 Right
|  | 59 | ENGINE EXHAUST CYL 5 Right
|  | 60 | ENGINE EXHAUST CYL 6 Right
|  | 61 | ENGINE EXHAUST PRE TURBO Left
|  | 62 | ENGINE EXHAUST PRE TURBO Right
|  | 63 | ENGINE AIR MANIFOLD Left
|  | 64 | ENGINE AIR MANIFOLD Right
65
66
67
|  | 68 | SUCTION PRESSURE SWITCH LOW
|  | 69 | STG 1DISCHARGE PRESSURE SWITCH HIGH
|  | 70 | STG 2 DISCHARGE PRESSURE SWITCH HIGH
|  | 71 | COMPRESSOR LUBE OIL PRESSURE LOW SWITCH
|  | 72 | CYLINDER LUBE PRESSURE LOW SWITCH
|  | 73 | ENGINE JACKET WATER FLOW SWITCH
|  | 74 | SPARE
|  | 75 | ENGINE LUBE OIL LEVEL LOW SWITCH
|  | 76 | COMP LUBE OIL LEVEL LOW SWITCH
|  | 77 | STG 1 SCRUBBER LEVEL HIGH SWITCH
|  | 78 | STG2 SCRUBBER LEVEL HIGH SWITCH
|  | 79 | SPARE
|  | 80 | SPARE
|  | 81 | LUBE NO FLOW CPI FSLL
|  | 82 | SPARE
|  | 83 | SPARE
|  | 84 | IGNITION FAULT
|  | 85 | COMPRESSOR CYLINDER VIBRATION #1
|  | 86 | COMPRESSOR CYLINDER VIBRATION #2
|  | 87 | COMPRESSOR COOLER VIBRATION #1
|  | 88 | COMPRESSOR COOLER VIBRATION#2
|  | 89 | SPARE
|  | 90 | SPARE
|  | 91 | SPARE
|  | 92 | SPARE
|  | 93 | SPARE
|  | 94 | SPARE
|  | 95 | REMOTE ESD
|  | 96 | PANEL EMERGENCY STOP
|  | 97 | Pre-Turbo Flywheel Exhaust Temp
|  | 98 | Post Turbo Flywheel Exhaust Temp
|  | 99 | Pre-Turbo Aux End Exhaust Temp
|  | 100 | Post Turbo Aux End Exhaust Temp
|  | 101 | Engine Bearing 1 Temp
|  | 102 | Engine Bearing 2 Temp
|  | 103 | Engine Bearing 3 Temp
|  | 104 | Engine Bearing 4 Temp
|  | 105 | Engine Bearing 5 Temp
|  | 106 | Engine Bearing 6 Temp
|  | 107 | Engine Bearing 7 Temp
|  | 108 | Engine Bearing 8 Temp
|  | 109 | Engine Bearing 9 Temp
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
|  | 161-170 | N/A
|  | 171 | OVERCRANK
|  | 254 | TIMERS ACTIVE
|  | 255 | RUNNING
40005 | Controller Module DS Output Status | 0 | Fuel | N/A
|  | 1 | Ignition | N/A
|  | 2 | Start Crank | N/A
|  | 3 | Auxiliary Lube | N/A
40006 | Fault Status | 0 | N/A
|  | 1 | LOW FAULT or DISCRETE FAULT
|  | 2 | HIGH FAULT
40020 | Digital output status for Terminal Module T1 | 0 | Fuel Valve
|  | 1 | Not Used
|  | 2 | Bypass Valve Open
|  | 3 | Blowdown Valve Close
|  | 4 | RUN STATUS
|  | 5 | ALARM HORN
|  | 6 | ALARM STATUS
|  | 7 | FAULT STATUS
40021 | Digital output status for Terminal Module T2 | 0
1
2
|  | 3 | ENGINE PRE LUBE
|  | 4 | STROBE LIGHT RUNNING GREEN
|  | 5 | STROBE LIGHT ALARM AMBER
|  | 6 | STROBE LIGHT FAULT RED
|  | 7 | STROBE LIGHT FLASH
40022 | Digital output status for Terminal Module T3 | 0
1
2
3
4
5
6
7
40023 | Digital output status for Terminal Module T4 | 0
1
2
3
4
5
6
7
40024 | Digital output status for Terminal Module T5 | 0
1
2
3
4
5
6
7
40090 | Terminal Module T1, Channels IN1 | N/A | Suction Stage 1 Pressure
40091 | Terminal Module T1, Channels IN2 | N/A | Discharge Stage 1 Pressure
40092 | Terminal Module T1, Channels IN3 | N/A
40093 | Terminal Module T1, Channels IN4 | N/A | Discharge Stage 2 Pressure
40094 | Terminal Module T1, Channels IN5 | N/A | 3rd Stage Suction Pressure
40095 | Terminal Module T1, Channels IN6 | N/A | 3rd Stage Discharge Pressure
40096 | Terminal Module T1, Channels IN7 | N/A | Compressor Lube Oil Pressure
40097 | Terminal Module T1, Channels IN8 | N/A | Engine Lube Oil Pressure
40098 | Terminal Module T1, Channels IN9 | N/A | GD01 Gas Detector- Comp side
40099 | Terminal Module T1, Channels IN10 | N/A | GD012 Gas Detector- Engine side
40100 | Terminal Module T1, Channels IN11 | N/A
40101 | Terminal Module T1, Channels IN12 | N/A
40102 | Terminal Module T1, Channels IN13 | N/A
40103 | Terminal Module T1, Channels IN14 | N/A
40104 | Terminal Module T1, Channels IN15 | N/A
40105 | Terminal Module T1, Channels IN16 | N/A
40106 | Terminal Module T1, Channels IN17 | N/A | Lube No Flow switch
40107 | Terminal Module T1, Channels IN18 | N/A | Engine Oil Level LSLL
40108 | Terminal Module T1, Channels IN19 | N/A | Compressor Oil Level LSLL
40109 | Terminal Module T1, Channels IN20 | N/A | Engine JW water Level LSLL
40110 | Terminal Module T1, Channels IN21 | N/A | Engine Aux Water Level LSLL
40111 | Terminal Module T1, Channels IN22 | N/A | Cooler Vibration VSHH
40112 | Terminal Module T1, Channels IN23 | N/A | Compressor Vibration VSHH
40113 | Terminal Module T1, Channels IN24 | N/A | Engine Vibration VSHH
40114 | Terminal Module T1, Channels IN25 | N/A | 1st STG Scrubber Level HIGH
40115 | Terminal Module T1, Channels IN26 | N/A | 2nd Stg Scrubber Level HIGH
40116 | Terminal Module T1, Channels IN27 | N/A | 3rd STG Scrubber Level HIGH
40117 | Terminal Module T1, Channels IN28 | N/A | CEC DSM Fault
40118 | Terminal Module T1, Channels IN29 | N/A | Engine Started
40119 | Terminal Module T1, Channels IN30 | N/A | Remote Stop USD
40120 | Terminal Module T1, Channels IN31 | N/A | Station ESD
40121 | Terminal Module T1, Channels IN32 | N/A | Panel Emergency Stop
40122 | Terminal Module T2, Channels IN1 | N/A | COMPRESSOR OIL TEMP
40123 | Terminal Module T2, Channels IN2 | N/A | CYL#1 DISCHARGE TEMP
40124 | Terminal Module T2, Channels IN3 | N/A | CYL#2 DISCHARGE TEMP
40125 | Terminal Module T2, Channels IN4 | N/A | CYL#3 DISCHARGE TEMP
40126 | Terminal Module T2, Channels IN5 | N/A | CYL#4 DISCHARGE TEMP
40127 | Terminal Module T2, Channels IN6 | N/A
40128 | Terminal Module T2, Channels IN7 | N/A
40129 | Terminal Module T2, Channels IN8 | N/A
40130 | Terminal Module T2, Channels IN9 | N/A | ENGINE OIL TEMP
40131 | Terminal Module T2, Channels IN10 | N/A | ENGINE JACKET WATER TEMP
40132 | Terminal Module T2, Channels IN11 | N/A | Engine ESD Right Side
40133 | Terminal Module T2, Channels IN12 | N/A | Engine ESD Left Side
40134 | Terminal Module T2, Channels IN13 | N/A
40135 | Terminal Module T2, Channels IN14 | N/A
40136 | Terminal Module T2, Channels IN15 | N/A
40137 | Terminal Module T2, Channels IN16 | N/A
40138 | Terminal Module T2, Channels IN17 | N/A | ENGINE EXHAUST CYL 1 Left
40139 | Terminal Module T2, Channels IN18 | N/A | ENGINE EXHAUST CYL 2 Left
40140 | Terminal Module T2, Channels IN19 | N/A | ENGINE EXHAUST CYL 3 Left
40141 | Terminal Module T2, Channels IN20 | N/A | ENGINE EXHAUST CYL 4 Left
40142 | Terminal Module T2, Channels IN21 | N/A | ENGINE EXHAUST CYL 5 Left
40143 | Terminal Module T2, Channels IN22 | N/A | ENGINE EXHAUST CYL 6 Left
40144 | Terminal Module T2, Channels IN23 | N/A | ENGINE EXHAUST CYL 1 Right
40145 | Terminal Module T2, Channels IN24 | N/A | ENGINE EXHAUST CYL 2 Right
40146 | Terminal Module T2, Channels IN25 | N/A | ENGINE EXHAUST CYL 3 Right
40147 | Terminal Module T2, Channels IN26 | N/A | ENGINE EXHAUST CYL 4 Right
40148 | Terminal Module T2, Channels IN27 | N/A | ENGINE EXHAUST CYL 5 Right
40149 | Terminal Module T2, Channels IN28 | N/A | ENGINE EXHAUST CYL 6 Right
40150 | Terminal Module T2, Channels IN29 | N/A | ENGINE EXHAUST PRE TURBO Left
40151 | Terminal Module T2, Channels IN30 | N/A | ENGINE EXHAUST PRE TURBO Right
40152 | Terminal Module T2, Channels IN31 | N/A | ENGINE AIR MANIFOLD Left
40153 | Terminal Module T2, Channels IN32 | N/A | ENGINE AIR MANIFOLD Right
40154 | Terminal Module T3, Channels IN1 | N/A
40155 | Terminal Module T3, Channels IN2 | N/A
40156 | Terminal Module T3, Channels IN3 | N/A
40157 | Terminal Module T3, Channels IN4 | N/A | SUCTION PRESSURE SWITCH LOW
40158 | Terminal Module T3, Channels IN5 | N/A | STG 1DISCHARGE PRESSURE SWITCH HIGH
40159 | Terminal Module T3, Channels IN6 | N/A | STG 2 DISCHARGE PRESSURE SWITCH HIGH
40160 | Terminal Module T3, Channels IN7 | N/A | COMPRESSOR LUBE OIL PRESSURE LOW SWITCH
40161 | Terminal Module T3, Channels IN8 | N/A | CYLINDER LUBE PRESSURE LOW SWITCH
40162 | Terminal Module T3, Channels IN9 | N/A | ENGINE JACKET WATER FLOW SWITCH
40163 | Terminal Module T3, Channels IN10 | N/A | SPARE
40164 | Terminal Module T3, Channels IN11 | N/A | ENGINE LUBE OIL LEVEL LOW SWITCH
40165 | Terminal Module T3, Channels IN12 | N/A | COMP LUBE OIL LEVEL LOW SWITCH
40166 | Terminal Module T3, Channels IN13 | N/A | STG 1 SCRUBBER LEVEL HIGH SWITCH
40167 | Terminal Module T3, Channels IN14 | N/A | STG2 SCRUBBER LEVEL HIGH SWITCH
40168 | Terminal Module T3, Channels IN15 | N/A | SPARE
40169 | Terminal Module T3, Channels IN16 | N/A | SPARE
40170 | Terminal Module T3, Channels IN17 | N/A | LUBE NO FLOW CPI FSLL
40171 | Terminal Module T3, Channels IN18 | N/A | SPARE
40172 | Terminal Module T3, Channels IN19 | N/A | SPARE
40173 | Terminal Module T3, Channels IN20 | N/A | IGNITION FAULT
40174 | Terminal Module T3, Channels IN21 | N/A | COMPRESSOR CYLINDER VIBRATION #1
40175 | Terminal Module T3, Channels IN22 | N/A | COMPRESSOR CYLINDER VIBRATION #2
40176 | Terminal Module T3, Channels IN23 | N/A | COMPRESSOR COOLER VIBRATION #1
40177 | Terminal Module T3, Channels IN24 | N/A | COMPRESSOR COOLER VIBRATION#2
40178 | Terminal Module T3, Channels IN25 | N/A | SPARE
40179 | Terminal Module T3, Channels IN26 | N/A | SPARE
40180 | Terminal Module T3, Channels IN27 | N/A | SPARE
40181 | Terminal Module T3, Channels IN28 | N/A | SPARE
40182 | Terminal Module T3, Channels IN29 | N/A | SPARE
40183 | Terminal Module T3, Channels IN30 | N/A | SPARE
40184 | Terminal Module T3, Channels IN31 | N/A | REMOTE ESD
40185 | Terminal Module T3, Channels IN32 | N/A | PANEL EMERGENCY STOP
40186 | Terminal Module T4, Channels IN1 | N/A | Pre-Turbo Flywheel Exhaust Temp
40187 | Terminal Module T4, Channels IN2 | N/A | Post Turbo Flywheel Exhaust Temp
40188 | Terminal Module T4, Channels IN3 | N/A | Pre-Turbo Aux End Exhaust Temp
40189 | Terminal Module T4, Channels IN4 | N/A | Post Turbo Aux End Exhaust Temp
40190 | Terminal Module T4, Channels IN5 | N/A | Engine Bearing 1 Temp
40191 | Terminal Module T4, Channels IN6 | N/A | Engine Bearing 2 Temp
40192 | Terminal Module T4, Channels IN7 | N/A | Engine Bearing 3 Temp
40193 | Terminal Module T4, Channels IN8 | N/A | Engine Bearing 4 Temp
40194 | Terminal Module T4, Channels IN9 | N/A | Engine Bearing 5 Temp
40195 | Terminal Module T4, Channels IN10 | N/A | Engine Bearing 6 Temp
40196 | Terminal Module T4, Channels IN11 | N/A | Engine Bearing 7 Temp
40197 | Terminal Module T4, Channels IN12 | N/A | Engine Bearing 8 Temp
40198 | Terminal Module T4, Channels IN13 | N/A | Engine Bearing 9 Temp
40199 | Terminal Module T4, Channels IN14 | N/A
40200 | Terminal Module T4, Channels IN15 | N/A
40201 | Terminal Module T4, Channels IN16 | N/A
40202 | Terminal Module T4, Channels IN17 | N/A
40203 | Terminal Module T4, Channels IN18 | N/A
40204 | Terminal Module T4, Channels IN19 | N/A
40205 | Terminal Module T4, Channels IN20 | N/A
40206 | Terminal Module T4, Channels IN21 | N/A
40207 | Terminal Module T4, Channels IN22 | N/A
40208 | Terminal Module T4, Channels IN23 | N/A
40209 | Terminal Module T4, Channels IN24 | N/A
40210 | Terminal Module T4, Channels IN25 | N/A
40211 | Terminal Module T4, Channels IN26 | N/A
40212 | Terminal Module T4, Channels IN27 | N/A
40213 | Terminal Module T4, Channels IN28 | N/A
40214 | Terminal Module T4, Channels IN29 | N/A
40215 | Terminal Module T4, Channels IN30 | N/A
40216 | Terminal Module T4, Channels IN31 | N/A
40217 | Terminal Module T4, Channels IN32 | N/A
40218 | Terminal Module T5, Channels IN1 | N/A
40219 | Terminal Module T5, Channels IN2 | N/A
40220 | Terminal Module T5, Channels IN3 | N/A
40221 | Terminal Module T5, Channels IN4 | N/A
40222 | Terminal Module T5, Channels IN5 | N/A
40223 | Terminal Module T5, Channels IN6 | N/A
40224 | Terminal Module T5, Channels IN7 | N/A
40225 | Terminal Module T5, Channels IN8 | N/A
40226 | Terminal Module T5, Channels IN9 | N/A
40227 | Terminal Module T5, Channels IN10 | N/A
40228 | Terminal Module T5, Channels IN11 | N/A
40229 | Terminal Module T5, Channels IN12 | N/A
40230 | Terminal Module T5, Channels IN13 | N/A
40231 | Terminal Module T5, Channels IN14 | N/A
40232 | Terminal Module T5, Channels IN15 | N/A
40233 | Terminal Module T5, Channels IN16 | N/A
40234 | Terminal Module T5, Channels IN17 | N/A
40235 | Terminal Module T5, Channels IN18 | N/A
40236 | Terminal Module T5, Channels IN19 | N/A
40237 | Terminal Module T5, Channels IN20 | N/A
40238 | Terminal Module T5, Channels IN21 | N/A
40239 | Terminal Module T5, Channels IN22 | N/A
40240 | Terminal Module T5, Channels IN23 | N/A
40241 | Terminal Module T5, Channels IN24 | N/A
40242 | Terminal Module T5, Channels IN25 | N/A
40243 | Terminal Module T5, Channels IN26 | N/A
40244 | Terminal Module T5, Channels IN27 | N/A
40245 | Terminal Module T5, Channels IN28 | N/A
40246 | Terminal Module T5, Channels IN29 | N/A
40247 | Terminal Module T5, Channels IN30 | N/A
40248 | Terminal Module T5, Channels IN31 | N/A
40249 | Terminal Module T5, Channels IN32 | N/A
40250 | T1:SP1 Speed in RPM | N/A | Engine RPM
40251 | T1:SP2 Speed in RPM | N/A
40252 | T2:SP1 Speed in RPM | N/A
40253 | T2:SP2 Speed in RPM | N/A
40254 | T3:SP1 Speed in RPM | N/A
40255 | T3:SP2 Speed in RPM | N/A
40256 | T4:SP1 Speed in RPM | N/A
40257 | T4:SP2 Speed in RPM | N/A
40258 | T5:SP1 Speed in RPM | N/A
40259 | T5:SP2 Speed in RPM | N/A
40260 | Analog Output in Percent (T1:AO1) | N/A | Suction Control Out
40261 | Analog Output in Percent (T1:AO2) | N/A | Engine Speed Control Out
40262 | Analog Output in Percent (T1:AO3) | N/A | Recycle Valve Control Out
40263 | Analog Output in Percent (T1:AO4) | N/A
40264 | Analog Output in Percent (T2:AO1) | N/A
40265 | Analog Output in Percent (T2:AO2) | N/A
40266 | Analog Output in Percent (T2:AO3) | N/A
40267 | Analog Output in Percent (T2:AO4) | N/A
40268 | Analog Output in Percent (T3:AO1) | N/A
40269 | Analog Output in Percent (T3:AO2) | N/A
40270 | Analog Output in Percent (T3:AO3) | N/A
40271 | Analog Output in Percent (T3:AO4) | N/A
40272 | Analog Output in Percent (T4:AO1) | N/A
40273 | Analog Output in Percent (T4:AO2) | N/A
40274 | Analog Output in Percent (T4:AO3) | N/A
40275 | Analog Output in Percent (T4:AO4) | N/A
40276 | Analog Output in Percent (T5:AO1) | N/A
40277 | Analog Output in Percent (T5:AO2) | N/A
40278 | Analog Output in Percent (T5:AO3) | N/A
40279 | Analog Output in Percent (T5:AO4) | N/A

## 32 bit registers
DE-4000 MODBUS 32 BIT REGISTER MAPPING (CURRENTLY AVAILABLE AT NODE# 200)
ADDRESS | DESCRIPTION | FUNCTION | DEVICE TAG
40001 | High Bits of T1: IN1 | Suction Stage 1 Pressure
40002 | Low Bits of T1:IN1
40003 | High Bits of T1: IN2 | Discharge Stage 1 Pressure
40004 | Low Bits of T1:IN2
40005 | High Bits of T1: IN3
40006 | Low Bits of T1:IN3
40007 | High Bits of T1: IN4 | Discharge Stage 2 Pressure
40008 | Low Bits of T1:IN4
40009 | High Bits of T1: IN5 | 3rd Stage Suction Pressure
40010 | Low Bits of T1:IN5
40011 | High Bits of T1: IN6 | 3rd Stage Discharge Pressure
40012 | Low Bits of T1:IN6
40013 | High Bits of T1: IN7 | Compressor Lube Oil Pressure
40014 | Low Bits of T1:IN7
40015 | High Bits of T1: IN8 | Engine Lube Oil Pressure
40016 | Low Bits of T1:IN8
40017 | High Bits of T1: IN9 | GD01 Gas Detector- Comp side
40018 | Low Bits of T1:IN9
40019 | High Bits of T1: IN10 | GD012 Gas Detector- Engine side
40020 | Low Bits of T1:IN10
40021 | High Bits of T1: IN11
40022 | Low Bits of T1:IN11
40023 | High Bits of T1: IN12
40024 | Low Bits of T1:IN12
40025 | High Bits of T1: IN13
40026 | Low Bits of T1:IN13
40027 | High Bits of T1: IN14
40028 | Low Bits of T1:IN14
40029 | High Bits of T1: IN15
40030 | Low Bits of T1:IN15
40031 | High Bits of T1: IN16
40032 | Low Bits of T1:IN16
40033 | High Bits of T1: IN17 | Lube No Flow switch
40034 | Low Bits of T1:IN17
40035 | High Bits of T1: IN18 | Engine Oil Level LSLL
40036 | Low Bits of T1:IN18
40037 | High Bits of T1: IN19 | Compressor Oil Level LSLL
40038 | Low Bits of T1:IN19
40039 | High Bits of T1: IN20 | Engine JW water Level LSLL
40040 | Low Bits of T1:IN20
40041 | High Bits of T1: IN21 | Engine Aux Water Level LSLL
40042 | Low Bits of T1:IN21
40043 | High Bits of T1: IN22 | Cooler Vibration VSHH
40044 | Low Bits of T1:IN22
40045 | High Bits of T1: IN23 | Compressor Vibration VSHH
40046 | Low Bits of T1:IN23
40047 | High Bits of T1: IN24 | Engine Vibration VSHH
40048 | Low Bits of T1:IN24
40049 | High Bits of T1: IN25 | 1st STG Scrubber Level HIGH
40050 | Low Bits of T1:IN25
40051 | High Bits of T1: IN26 | 2nd Stg Scrubber Level HIGH
40052 | Low Bits of T1:IN26
40053 | High Bits of T1: IN27 | 3rd STG Scrubber Level HIGH
40054 | Low Bits of T1:IN27
40055 | High Bits of T1: IN28 | CEC DSM Fault
40056 | Low Bits of T1:IN28
40057 | High Bits of T1: IN29 | Engine Started
40058 | Low Bits of T1:IN29
40059 | High Bits of T1: IN30 | Remote Stop USD
40060 | Low Bits of T1:IN30
40061 | High Bits of T1: IN31 | Station ESD
40062 | Low Bits of T1:IN31
40063 | High Bits of T1: IN32 | Panel Emergency Stop
40064 | Low Bits of T1:IN32
40065 | High Bits of T2: IN1 | COMPRESSOR OIL TEMP
40066 | Low Bits of T2:IN1
40067 | High Bits of T2: IN2 | CYL#1 DISCHARGE TEMP
40068 | Low Bits of T2:IN2
40069 | High Bits of T2: IN3 | CYL#2 DISCHARGE TEMP
40070 | Low Bits of T2:IN3
40071 | High Bits of T2: IN4 | CYL#3 DISCHARGE TEMP
40072 | Low Bits of T2:IN4
40073 | High Bits of T2: IN5 | CYL#4 DISCHARGE TEMP
40074 | Low Bits of T2:IN5
40075 | High Bits of T2: IN6
40076 | Low Bits of T2:IN6
40077 | High Bits of T2: IN7
40078 | Low Bits of T2:IN7
40079 | High Bits of T2: IN8
40080 | Low Bits of T2:IN8
40081 | High Bits of T2: IN9 | ENGINE OIL TEMP
40082 | Low Bits of T2:IN9
40083 | High Bits of T2: IN10 | ENGINE JACKET WATER TEMP
40084 | Low Bits of T2:IN10
40085 | High Bits of T2: IN11 | Engine ESD Right Side
40086 | Low Bits of T2:IN11
40087 | High Bits of T2: IN12 | Engine ESD Left Side
40088 | Low Bits of T2:IN12
40089 | High Bits of T2: IN13
40090 | Low Bits of T2:IN13
40091 | High Bits of T2: IN14
40092 | Low Bits of T2:IN14
40093 | High Bits of T2: IN15
40094 | Low Bits of T2:IN15
40095 | High Bits of T2: IN16
40096 | Low Bits of T2:IN16
40097 | High Bits of T2: IN17 | ENGINE EXHAUST CYL 1 Left
40098 | Low Bits of T2:IN17
40099 | High Bits of T2: IN18 | ENGINE EXHAUST CYL 2 Left
40100 | Low Bits of T2:IN18
40101 | High Bits of T2: IN19 | ENGINE EXHAUST CYL 3 Left
40102 | Low Bits of T2:IN19
40103 | High Bits of T2: IN20 | ENGINE EXHAUST CYL 4 Left
40104 | Low Bits of T2:IN20
40105 | High Bits of T2: IN21 | ENGINE EXHAUST CYL 5 Left
40106 | Low Bits of T2:IN21
40107 | High Bits of T2: IN22 | ENGINE EXHAUST CYL 6 Left
40108 | Low Bits of T2:IN22
40109 | High Bits of T2: IN23 | ENGINE EXHAUST CYL 1 Right
40110 | Low Bits of T2:IN23
40111 | High Bits of T2: IN24 | ENGINE EXHAUST CYL 2 Right
40112 | Low Bits of T2:IN24
40113 | High Bits of T2: IN25 | ENGINE EXHAUST CYL 3 Right
40114 | Low Bits of T2:IN25
40115 | High Bits of T2: IN26 | ENGINE EXHAUST CYL 4 Right
40116 | Low Bits of T2:IN26
40117 | High Bits of T2: IN27 | ENGINE EXHAUST CYL 5 Right
40118 | Low Bits of T2:IN27
40119 | High Bits of T2: IN28 | ENGINE EXHAUST CYL 6 Right
40120 | Low Bits of T2:IN28
40121 | High Bits of T2: IN29 | ENGINE EXHAUST PRE TURBO Left
40122 | Low Bits of T2:IN29
40123 | High Bits of T2: IN30 | ENGINE EXHAUST PRE TURBO Right
40124 | Low Bits of T2:IN30
40125 | High Bits of T2: IN31 | ENGINE AIR MANIFOLD Left
40126 | Low Bits of T2:IN31
40127 | High Bits of T2: IN32 | ENGINE AIR MANIFOLD Right
40128 | Low Bits of T2:IN32
40129 | High Bits of T3: IN1 | N/A | N/A
40130 | Low Bits of T3:IN1
40131 | High Bits of T3: IN2 | N/A | N/A
40132 | Low Bits of T3:IN2
40133 | High Bits of T3: IN3 | N/A | N/A
40134 | Low Bits of T3:IN3
40135 | High Bits of T3: IN4 | N/A | N/A
40136 | Low Bits of T3:IN4
40137 | High Bits of T3: IN5 | N/A | N/A
40138 | Low Bits of T3:IN5
40139 | High Bits of T3: IN6 | N/A | N/A
40140 | Low Bits of T3:IN6
40141 | High Bits of T3: IN7 | N/A | N/A
40142 | Low Bits of T3:IN7
40143 | High Bits of T3: IN8 | N/A | N/A
40144 | Low Bits of T3:IN8
40145 | High Bits of T3: IN9 | N/A | N/A
40146 | Low Bits of T3:IN9
40147 | High Bits of T3: IN10 | N/A | N/A
40148 | Low Bits of T3:IN10
40149 | High Bits of T3: IN11 | N/A | N/A
40150 | Low Bits of T3:IN11
40151 | High Bits of T3: IN12 | N/A | N/A
40152 | Low Bits of T3:IN12
40153 | High Bits of T3: IN13 | N/A | N/A
40154 | Low Bits of T3:IN13
40155 | High Bits of T3: IN14 | N/A | N/A
40156 | Low Bits of T3:IN14
40157 | High Bits of T3: IN15 | N/A | N/A
40158 | Low Bits of T3:IN15
40159 | High Bits of T3: IN16 | N/A | N/A
40160 | Low Bits of T3:IN16
40161 | High Bits of T3: IN17 | N/A | N/A
40162 | Low Bits of T3:IN17
40163 | High Bits of T3: IN18 | N/A | N/A
40164 | Low Bits of T3:IN18
40165 | High Bits of T3: IN19 | N/A | N/A
40166 | Low Bits of T3:IN19
40167 | High Bits of T3: IN20 | N/A | N/A
40168 | Low Bits of T3:IN20
40169 | High Bits of T3: IN21 | N/A | N/A
40170 | Low Bits of T3:IN21
40171 | High Bits of T3: IN22 | N/A | N/A
40172 | Low Bits of T3:IN22
40173 | High Bits of T3: IN23 | N/A | N/A
40174 | Low Bits of T3:IN23
40175 | High Bits of T3: IN24 | N/A | N/A
40176 | Low Bits of T3:IN24
40177 | High Bits of T3: IN25 | N/A | N/A
40178 | Low Bits of T3:IN25
40179 | High Bits of T3: IN26 | N/A | N/A
40180 | Low Bits of T3:IN26
40181 | High Bits of T3: IN27 | N/A | N/A
40182 | Low Bits of T3:IN27
40183 | High Bits of T3: IN28 | N/A | N/A
40184 | Low Bits of T3:IN28
40185 | High Bits of T3: IN29 | N/A | N/A
40186 | Low Bits of T3:IN29
40187 | High Bits of T3: IN30 | N/A | N/A
40188 | Low Bits of T3:IN30
40189 | High Bits of T3: IN31 | N/A | N/A
40190 | Low Bits of T3:IN31
40191 | High Bits of T3: IN32 | N/A | N/A
40192 | Low Bits of T3:IN32
40193 | High Bits of T4: IN1 | N/A | N/A
40194 | Low Bits of T4:IN1
40195 | High Bits of T4: IN2 | N/A | N/A
40196 | Low Bits of T4:IN2
40197 | High Bits of T4: IN3 | N/A | N/A
40198 | Low Bits of T4:IN3
40199 | High Bits of T4: IN4 | N/A | N/A
40200 | Low Bits of T4:IN4
40201 | High Bits of T4: IN5 | N/A | N/A
40202 | Low Bits of T4:IN5
40203 | High Bits of T4: IN6 | N/A | N/A
40204 | Low Bits of T4:IN6
40205 | High Bits of T4: IN7 | N/A | N/A
40206 | Low Bits of T4:IN7
40207 | High Bits of T4: IN8 | N/A | N/A
40208 | Low Bits of T4:IN8
40209 | High Bits of T4: IN9 | N/A | N/A
40210 | Low Bits of T4:IN9
40211 | High Bits of T4: IN10 | N/A | N/A
40212 | Low Bits of T4:IN10
40213 | High Bits of T4: IN11 | N/A | N/A
40214 | Low Bits of T4:IN11
40215 | High Bits of T4: IN12 | N/A | N/A
40216 | Low Bits of T4:IN12
40217 | High Bits of T4: IN13 | N/A | N/A
40218 | Low Bits of T4:IN13
40219 | High Bits of T4: IN14 | N/A | N/A
40220 | Low Bits of T4:IN14
40221 | High Bits of T4: IN15 | N/A | N/A
40222 | Low Bits of T4:IN15
40223 | High Bits of T4: IN16 | N/A | N/A
40224 | Low Bits of T4:IN16
40225 | High Bits of T4: IN17 | N/A | N/A
40226 | Low Bits of T4:IN17
40227 | High Bits of T4: IN18 | N/A | N/A
40228 | Low Bits of T4:IN18
40229 | High Bits of T4: IN19 | N/A | N/A
40230 | Low Bits of T4:IN19
40231 | High Bits of T4: IN20 | N/A | N/A
40232 | Low Bits of T4:IN20
40233 | High Bits of T4: IN21 | N/A | N/A
40234 | Low Bits of T4:IN21
40235 | High Bits of T4: IN22 | N/A | N/A
40236 | Low Bits of T4:IN22
40237 | High Bits of T4: IN23 | N/A | N/A
40238 | Low Bits of T4:IN23
40239 | High Bits of T4: IN24 | N/A | N/A
40240 | Low Bits of T4:IN24
40241 | High Bits of T4: IN25 | N/A | N/A
40242 | Low Bits of T4:IN25
40243 | High Bits of T4: IN26 | N/A | N/A
40244 | Low Bits of T4:IN26
40245 | High Bits of T4: IN27 | N/A | N/A
40246 | Low Bits of T4:IN27
40247 | High Bits of T4: IN28 | N/A | N/A
40248 | Low Bits of T4:IN28
40249 | High Bits of T4: IN29 | N/A | N/A
40250 | Low Bits of T4:IN29
40251 | High Bits of T4: IN30 | N/A | N/A
40252 | Low Bits of T4:IN30
40253 | High Bits of T4: IN31 | N/A | N/A
40254 | Low Bits of T4:IN31
40255 | High Bits of T4: IN32 | N/A | N/A
40256 | Low Bits of T4:IN32
40257 | High Bits of T5: IN1 | N/A | N/A
40258 | Low Bits of T5:IN1
40259 | High Bits of T5: IN2 | N/A | N/A
40260 | Low Bits of T5:IN2
40261 | High Bits of T5: IN3 | N/A | N/A
40262 | Low Bits of T5:IN3
40263 | High Bits of T5: IN4 | N/A | N/A
40264 | Low Bits of T5:IN4
40265 | High Bits of T5: IN5 | N/A | N/A
40266 | Low Bits of T5:IN5
40267 | High Bits of T5: IN6 | N/A | N/A
40268 | Low Bits of T5:IN6
40269 | High Bits of T5: IN7 | N/A | N/A
40270 | Low Bits of T5:IN7
40271 | High Bits of T5: IN8 | N/A | N/A
40272 | Low Bits of T5:IN8
40273 | High Bits of T5: IN9 | N/A | N/A
40274 | Low Bits of T5:IN9
40275 | High Bits of T5: IN10 | N/A | N/A
40276 | Low Bits of T5:IN10
40277 | High Bits of T5: IN11 | N/A | N/A
40278 | Low Bits of T5:IN11
40279 | High Bits of T5: IN12 | N/A | N/A
40280 | Low Bits of T5:IN12
40281 | High Bits of T5: IN13 | N/A | N/A
40282 | Low Bits of T5:IN13
40283 | High Bits of T5: IN14 | N/A | N/A
40284 | Low Bits of T5:IN14
40285 | High Bits of T5: IN15 | N/A | N/A
40286 | Low Bits of T5:IN15
40287 | High Bits of T5: IN16 | N/A | N/A
40288 | Low Bits of T5:IN16
40289 | High Bits of T5: IN17 | N/A | N/A
40290 | Low Bits of T5:IN17
40291 | High Bits of T5: IN18 | N/A | N/A
40292 | Low Bits of T5:IN18
40293 | High Bits of T5: IN19 | N/A | N/A
40294 | Low Bits of T5:IN19
40295 | High Bits of T5: IN20 | N/A | N/A
40296 | Low Bits of T5:IN20
40297 | High Bits of T5: IN21 | N/A | N/A
40298 | Low Bits of T5:IN21
40299 | High Bits of T5: IN22 | N/A | N/A
40300 | Low Bits of T5:IN22
40301 | High Bits of T5: IN23 | N/A | N/A
40302 | Low Bits of T5:IN23
40303 | High Bits of T5: IN24 | N/A | N/A
40304 | Low Bits of T5:IN24
40305 | High Bits of T5: IN25 | N/A | N/A
40306 | Low Bits of T5:IN25
40307 | High Bits of T5: IN26 | N/A | N/A
40308 | Low Bits of T5:IN26
40309 | High Bits of T5: IN27 | N/A | N/A
40310 | Low Bits of T5:IN27
40311 | High Bits of T5: IN28 | N/A | N/A
40312 | Low Bits of T5:IN28
40313 | High Bits of T5: IN29 | N/A | N/A
40314 | Low Bits of T5:IN29
40315 | High Bits of T5: IN30 | N/A | N/A
40316 | Low Bits of T5:IN30
40317 | High Bits of T5: IN31 | N/A | N/A
40318 | Low Bits of T5:IN31
40319 | High Bits of T5: IN32 | N/A | N/A
40320 | Low Bits of T5:IN32
40399
PID #1 (all values are 32 bit floating point)
40402:40403 | ENABLE (0 = Disable, 1 = Enable) | See Program for Additional Information
40404:40405 | P-Factor
40406:40407 | I-Factor
40408:40409 | D-Factor
40410:40411 | Max limit
40412:40413 | Min limit
40414:40415 | Input Terminal (1 - 5)
40416:40417 | Input Channel (1 - 32)
40418:40419 | Output Terminal (1 - 5)
40420:40421 | Output Channel (1 - 4)
40422:40423 | Deadband
40424:40425 | Setpoint
PID #2 (all values are 32 bit floating point)
40432:40433 | ENABLE (0 = Disable, 1 = Enable) | See Program for Additional Information
40434:40435 | P-Factor
40436:40437 | I-Factor
40438:40439 | D-Factor
40440:40441 | Max limit
40442:40443 | Min limit
40444:40445 | Input Terminal (1 - 5)
40446:40447 | Input Channel (1 - 32)
40448:40449 | Output Terminal (1 - 5)
40450:40451 | Output Channel (1 - 4)
40452:40453 | Deadband
40454:40455 | Setpoint
PID #3 (all values are 32 bit floating point)
40462:40463 | ENABLE (0 = Disable, 1 = Enable) | See Program for Additional Information
40464:40465 | P-Factor
40466:40467 | I-Factor
40468:40469 | D-Factor
40470:40471 | Max limit
40472:40473 | Min limit
40474:40475 | Input Terminal (1 - 5)
40476:40477 | Input Channel (1 - 32)
40478:40479 | Output Terminal (1 - 5)
40480:40481 | Output Channel (1 - 4)
40482:40483 | Deadband
40484:40485 | Setpoint
PID #4 (all values are 32 bit floating point)
40492:40493 | ENABLE (0 = Disable, 1 = Enable) | See Program for Additional Information
40494:40495 | P-Factor
40496:40497 | I-Factor
40498:40499 | D-Factor
40500:40501 | Max limit
40502:40503 | Min limit
40504:40505 | Input Terminal (1 - 5)
40506:40507 | Input Channel (1 - 32)
40508:40509 | Output Terminal (1 - 5)
40510:40511 | Output Channel (1 - 4)
40512:40513 | Deadband
40514:40515 | Setpoint
PID #5 (all values are 32 bit floating point)
40522:40523 | ENABLE (0 = Disable, 1 = Enable) | See Program for Additional Information
40524:40525 | P-Factor
40526:40527 | I-Factor
40528:40529 | D-Factor
40530:40531 | Max limit
40532:40533 | Min limit
40534:40535 | Input Terminal (1 - 5)
40536:40537 | Input Channel (1 - 32)
40538:40539 | Output Terminal (1 - 5)
40540:40541 | Output Channel (1 - 4)
40542:40543 | Deadband
40544:40545 | Setpoint
PID #6 (all values are 32 bit floating point)
40552:40553 | ENABLE (0 = Disable, 1 = Enable) | See Program for Additional Information
40554:40555 | P-Factor
40556:40557 | I-Factor
40558:40559 | D-Factor
40560:40561 | Max limit
40562:40563 | Min limit
40564:40565 | Input Terminal (1 - 5)
40566:40567 | Input Channel (1 - 32)
40568:40569 | Output Terminal (1 - 5)
40570:40571 | Output Channel (1 - 4)
40572:40573 | Deadband
40574:40575 | Setpoint
PID #7 (all values are 32 bit floating point)
40582:40583 | ENABLE (0 = Disable, 1 = Enable) | See Program for Additional Information
40584:40585 | P-Factor
40586:40587 | I-Factor
40588:40589 | D-Factor
40590:40591 | Max limit
40592:40593 | Min limit
40594:40595 | Input Terminal (1 - 5)
40596:40597 | Input Channel (1 - 32)
40598:40599 | Output Terminal (1 - 5)
40600:40601 | Output Channel (1 - 4)
40602:40603 | Deadband
40604:40605 | Setpoint
PID #8 (all values are 32 bit floating point)
40612:40613 | ENABLE (0 = Disable, 1 = Enable) | See Program for Additional Information
40614:40615 | P-Factor
40616:40617 | I-Factor
40618:40619 | D-Factor
40620:40621 | Max limit
40622:40623 | Min limit
40624:40625 | Input Terminal (1 - 5)
40626:40627 | Input Channel (1 - 32)
40628:40629 | Output Terminal (1 - 5)
40630:40631 | Output Channel (1 - 4)
40632:40633 | Deadband
40634:40635 | Setpoint
PID #9 (all values are 32 bit floating point)
40642:40643 | ENABLE (0 = Disable, 1 = Enable) | See Program for Additional Information
40644:40645 | P-Factor
40646:40647 | I-Factor
40648:40649 | D-Factor
40650:40651 | Max limit
40652:40653 | Min limit
40654:40655 | Input Terminal (1 - 5)
40656:40657 | Input Channel (1 - 32)
40658:40659 | Output Terminal (1 - 5)
40660:40661 | Output Channel (1 - 4)
40662:40663 | Deadband
40664:40665 | Setpoint
PID #10 (all values are 32 bit floating point)
40672:40673 | ENABLE (0 = Disable, 1 = Enable) | See Program for Additional Information
40674:40675 | P-Factor
40676:40677 | I-Factor
40678:40679 | D-Factor
40680:40681 | Max limit
40682:40683 | Min limit
40684:40685 | Input Terminal (1 - 5)
40686:40687 | Input Channel (1 - 32)
40688:40689 | Output Terminal (1 - 5)
40690:40691 | Output Channel (1 - 4)
40692:40693 | Deadband
40694:40695 | Setpoint
40700 | Main Key Command Register Write 1 for Start Write 2 for Reset Write 3 for Stop Write 4 for Cancel Timers
40701 | Start Key Command (write any value to start)
40702 | Reset Key Command (write any value to reset)
40703 | Stop Key Command (write any value to stop)
40704 | Cancel Timers Key Command (write any value to Cancel Timers)
Global/Control (all values are 32 bit floats)
40800:40801 | Input #1 Enable
40802:40803 | Input #2 Enable
40804:40805 | Input #1 0% Output
40806:40807 | Input #1 100% Output
40808:40809 | Input #2 0% Output
40810:40811 | Input #2 100% Output
40812:40813 | Input #1 Linear/PID (0 = Linear, 1 = PID)
40814:40815 | Input #2 Linear/PID (0 = Linear, 1 = PID)
40816:40817 | Input #1 Terminal (1 - 5)
40818:40819 | Input #1 Channel (1 - 32)
40820:40821 | Input #2 Terminal (1 - 5)
40822:40823 | Input #2 Channel (1 - 32)
40824:40825 | Output #1 Terminal (1 - 5)
40826:40827 | Output #1 Channel (1 - 4)
40828:40829 | Output #2 Terminal (1 - 5)
40830:40831 | Output #2 Channel (1 - 4)
40832:40833 | Output #1 Low
40834:40835 | Output #1 High
40836:40837 | Output #2 Low
40838:40839 | Output #2 High
40840:40841 | Output #1 Ramp Rate
40842:40843 | Output #2 Ramp Rate
40844:40845 | Output #1 Reverse Action (0 = Normal, 1 = Reverse)
40846:40847 | Output #2 Reverse Action (0 = Normal, 1 = Reverse)
40848:40849 | Input #1 P-Factor
40850:40851 | Input #1 I-Factor
40852:40853 | Input #1 D-Factor
40854:40855 | Input #2 P-Factor
40856:40857 | Input #2 I-Factor
40858:40859 | Input #2 D-Factor
40860:40861 | Auto/Manual Toggle Input Terminal (1 - 5)
40862:40863 | Auto/Manual Toggle Input Channel (1 - 32)
40864:40865 | SpeedControl Mode (0 = Manual, 1 = Auto)
40866:40867 | Manual Speed (value in RPM)
41001 - 41998 | Register Mirror Test Area (Any value written to these registers will be able to be read starting at register 30001. For example you can write a 32 bit value at 41001,41002 and read it at 30001, 30002)
42000:42001 | Term 1, Input 1 High Safety Setpoint | Suction Stage 1 Pressure
42002:42003 | Term 1, Input 1 Low Safety Setpoint
42100:42101 | Term 1, Input 2 High Safety Setpoint | Discharge Stage 1 Pressure
42102:42103 | Term 1, Input 2 Low Safety Setpoint
42200:42201 | Term 1, Input 3 High Safety Setpoint
42202:42203 | Term 1, Input 3 Low Safety Setpoint
42300:42301 | Term 1, Input 4 High Safety Setpoint | Discharge Stage 2 Pressure
42302:42303 | Term 1, Input 4 Low Safety Setpoint
42400:42401 | Term 1, Input 5 High Safety Setpoint | 3rd Stage Suction Pressure
42402:42403 | Term 1, Input 5 Low Safety Setpoint
42500:42501 | Term 1, Input 6 High Safety Setpoint | 3rd Stage Discharge Pressure
42502:42503 | Term 1, Input 6 Low Safety Setpoint
42600:42601 | Term 1, Input 7 High Safety Setpoint | Compressor Lube Oil Pressure
42602:42603 | Term 1, Input 7 Low Safety Setpoint
42700:42701 | Term 1, Input 8 High Safety Setpoint | Engine Lube Oil Pressure
42702:42703 | Term 1, Input 8 Low Safety Setpoint
42800:42801 | Term 1, Input 9 High Safety Setpoint | GD01 Gas Detector- Comp side
42802:42803 | Term 1, Input 9 Low Safety Setpoint
42900:42901 | Term 1, Input 10 High Safety Setpoint | GD012 Gas Detector- Engine side
42902:42903 | Term 1, Input 10 Low Safety Setpoint
43000:43001 | Term 1, Input 11 High Safety Setpoint
43002:43003 | Term 1, Input 11 Low Safety Setpoint
43100:43101 | Term 1, Input 12 High Safety Setpoint
43102:43103 | Term 1, Input 12 Low Safety Setpoint
43200:43201 | Term 1, Input 13 High Safety Setpoint
43202:43203 | Term 1, Input 13 Low Safety Setpoint
43300:43301 | Term 1, Input 14 High Safety Setpoint
43302:43303 | Term 1, Input 14 Low Safety Setpoint
43400:43401 | Term 1, Input 15 High Safety Setpoint
43402:43403 | Term 1, Input 15 Low Safety Setpoint
43500:43501 | Term 1, Input 16 High Safety Setpoint
43502:43503 | Term 1, Input 16 Low Safety Setpoint
43600:43601 | Term 1, Input 17 High Safety Setpoint | Lube No Flow switch
43602:43603 | Term 1, Input 17 Low Safety Setpoint
43700:43701 | Term 1, Input 18 High Safety Setpoint | Engine Oil Level LSLL
43702:43703 | Term 1, Input 18 Low Safety Setpoint
43800:43801 | Term 1, Input 19 High Safety Setpoint | Compressor Oil Level LSLL
43802:43803 | Term 1, Input 19 Low Safety Setpoint
43900:43901 | Term 1, Input 20 High Safety Setpoint | Engine JW water Level LSLL
43902:43903 | Term 1, Input 20 Low Safety Setpoint
44000:44001 | Term 1, Input 21 High Safety Setpoint | Engine Aux Water Level LSLL
44002:44003 | Term 1, Input 21 Low Safety Setpoint
44100:44101 | Term 1, Input 22 High Safety Setpoint | Cooler Vibration VSHH
44102:44103 | Term 1, Input 22 Low Safety Setpoint
44200:44201 | Term 1, Input 23 High Safety Setpoint | Compressor Vibration VSHH
44202:44203 | Term 1, Input 23 Low Safety Setpoint
44300:44301 | Term 1, Input 24 High Safety Setpoint | Engine Vibration VSHH
44302:44303 | Term 1, Input 24 Low Safety Setpoint
44400:44401 | Term 1, Input 25 High Safety Setpoint | 1st STG Scrubber Level HIGH
44402:44403 | Term 1, Input 25 Low Safety Setpoint
44500:44501 | Term 1, Input 26 High Safety Setpoint | 2nd Stg Scrubber Level HIGH
44502:44503 | Term 1, Input 26 Low Safety Setpoint
44600:44601 | Term 1, Input 27 High Safety Setpoint | 3rd STG Scrubber Level HIGH
44602:44603 | Term 1, Input 27 Low Safety Setpoint
44700:44701 | Term 1, Input 28 High Safety Setpoint | CEC DSM Fault
44702:44703 | Term 1, Input 28 Low Safety Setpoint
44800:44801 | Term 1, Input 29 High Safety Setpoint | Engine Started
44802:44803 | Term 1, Input 29 Low Safety Setpoint
44900:44901 | Term 1, Input 30 High Safety Setpoint | Remote Stop USD
44902:44903 | Term 1, Input 30 Low Safety Setpoint
45000:45001 | Term 1, Input 31 High Safety Setpoint | Station ESD
45002:45003 | Term 1, Input 31 Low Safety Setpoint
45100:45101 | Term 1, Input 32 High Safety Setpoint | Panel Emergency Stop
45102:45103 | Term 1, Input 32 Low Safety Setpoint
45200:45201 | Term 2, Input 1 High Safety Setpoint | COMPRESSOR OIL TEMP
45202:45203 | Term 2, Input 1 Low Safety Setpoint
45300:45301 | Term 2, Input 2 High Safety Setpoint | CYL#1 DISCHARGE TEMP
45302:45303 | Term 2, Input 2 Low Safety Setpoint
45400:45401 | Term 2, Input 3 High Safety Setpoint | CYL#2 DISCHARGE TEMP
45402:45403 | Term 2, Input 3 Low Safety Setpoint
45500:45501 | Term 2, Input 4 High Safety Setpoint | CYL#3 DISCHARGE TEMP
45502:45503 | Term 2, Input 4 Low Safety Setpoint
45600:45601 | Term 2, Input 5 High Safety Setpoint | CYL#4 DISCHARGE TEMP
45602:45603 | Term 2, Input 5 Low Safety Setpoint
45700:45701 | Term 2, Input 6 High Safety Setpoint
45702:45703 | Term 2, Input 6 Low Safety Setpoint
45800:45801 | Term 2, Input 7 High Safety Setpoint
45802:45803 | Term 2, Input 7 Low Safety Setpoint
45900:45901 | Term 2, Input 8 High Safety Setpoint
45902:45903 | Term 2, Input 8 Low Safety Setpoint
46000:46001 | Term 2, Input 9 High Safety Setpoint | ENGINE OIL TEMP
46002:46003 | Term 2, Input 9 Low Safety Setpoint
46100:46101 | Term 2, Input 10 High Safety Setpoint | ENGINE JACKET WATER TEMP
46102:46103 | Term 2, Input 10 Low Safety Setpoint
46200:46201 | Term 2, Input 11 High Safety Setpoint | Engine ESD Right Side
46202:46203 | Term 2, Input 11 Low Safety Setpoint
46300:46301 | Term 2, Input 12 High Safety Setpoint | Engine ESD Left Side
46302:46303 | Term 2, Input 12 Low Safety Setpoint
46400:46401 | Term 2, Input 13 High Safety Setpoint
46402:46403 | Term 2, Input 13 Low Safety Setpoint
46500:46501 | Term 2, Input 14 High Safety Setpoint
46502:46503 | Term 2, Input 14 Low Safety Setpoint
46600:46601 | Term 2, Input 15 High Safety Setpoint
46602:46603 | Term 2, Input 15 Low Safety Setpoint
46700:46701 | Term 2, Input 16 High Safety Setpoint
46702:46703 | Term 2, Input 16 Low Safety Setpoint
46800:46801 | Term 2, Input 17 High Safety Setpoint | ENGINE EXHAUST CYL 1 Left
46802:46803 | Term 2, Input 17 Low Safety Setpoint
46900:46901 | Term 2, Input 18 High Safety Setpoint | ENGINE EXHAUST CYL 2 Left
46902:46903 | Term 2, Input 18 Low Safety Setpoint
47000:47001 | Term 2, Input 19 High Safety Setpoint | ENGINE EXHAUST CYL 3 Left
47002:47003 | Term 2, Input 19 Low Safety Setpoint
47100:47101 | Term 2, Input 20 High Safety Setpoint | ENGINE EXHAUST CYL 4 Left
47102:47103 | Term 2, Input 20 Low Safety Setpoint
47200:47201 | Term 2, Input 21 High Safety Setpoint | ENGINE EXHAUST CYL 5 Left
47202:47203 | Term 2, Input 21 Low Safety Setpoint
47300:47301 | Term 2, Input 22 High Safety Setpoint | ENGINE EXHAUST CYL 6 Left
47302:47303 | Term 2, Input 22 Low Safety Setpoint
47400:47401 | Term 2, Input 23 High Safety Setpoint | ENGINE EXHAUST CYL 1 Right
47402:47403 | Term 2, Input 23 Low Safety Setpoint
47500:47501 | Term 2, Input 24 High Safety Setpoint | ENGINE EXHAUST CYL 2 Right
47502:47503 | Term 2, Input 24 Low Safety Setpoint
47600:47601 | Term 2, Input 25 High Safety Setpoint | ENGINE EXHAUST CYL 3 Right
47602:47603 | Term 2, Input 25 Low Safety Setpoint
47700:47701 | Term 2, Input 26 High Safety Setpoint | ENGINE EXHAUST CYL 4 Right
47702:47703 | Term 2, Input 26 Low Safety Setpoint
47800:47801 | Term 2, Input 27 High Safety Setpoint | ENGINE EXHAUST CYL 5 Right
47802:47803 | Term 2, Input 27 Low Safety Setpoint
47900:47901 | Term 2, Input 28 High Safety Setpoint | ENGINE EXHAUST CYL 6 Right
47902:47903 | Term 2, Input 28 Low Safety Setpoint
48000:48001 | Term 2, Input 29 High Safety Setpoint | ENGINE EXHAUST PRE TURBO Left
48002:48003 | Term 2, Input 29 Low Safety Setpoint
48100:48101 | Term 2, Input 30 High Safety Setpoint | ENGINE EXHAUST PRE TURBO Right
48102:48103 | Term 2, Input 30 Low Safety Setpoint
48200:48201 | Term 2, Input 31 High Safety Setpoint | ENGINE AIR MANIFOLD Left
48202:48203 | Term 2, Input 31 Low Safety Setpoint
48300:48301 | Term 2, Input 32 High Safety Setpoint | ENGINE AIR MANIFOLD Right
48302:48303 | Term 2, Input 32 Low Safety Setpoint
48400:48401 | Term 3, Input 1 High Safety Setpoint | N/A | N/A
48402:48403 | Term 3, Input 1 Low Safety Setpoint
48500:48501 | Term 3, Input 2 High Safety Setpoint | N/A | N/A
48502:48503 | Term 3, Input 2 Low Safety Setpoint
48600:48601 | Term 3, Input 3 High Safety Setpoint | N/A | N/A
48602:48603 | Term 3, Input 3 Low Safety Setpoint
48700:48701 | Term 3, Input 4 High Safety Setpoint | N/A | N/A
48702:48703 | Term 3, Input 4 Low Safety Setpoint
48800:48801 | Term 3, Input 5 High Safety Setpoint | N/A | N/A
48802:48803 | Term 3, Input 5 Low Safety Setpoint
48900:48901 | Term 3, Input 6 High Safety Setpoint | N/A | N/A
48902:48903 | Term 3, Input 6 Low Safety Setpoint
49000:49001 | Term 3, Input 7 High Safety Setpoint | N/A | N/A
49002:49003 | Term 3, Input 7 Low Safety Setpoint
49100:49101 | Term 3, Input 8 High Safety Setpoint | N/A | N/A
49102:49103 | Term 3, Input 8 Low Safety Setpoint
49200:49201 | Term 3, Input 9 High Safety Setpoint | N/A | N/A
49202:49203 | Term 3, Input 9 Low Safety Setpoint
49300:49301 | Term 3, Input 10 High Safety Setpoint | N/A | N/A
49302:49303 | Term 3, Input 10 Low Safety Setpoint
49400:49401 | Term 3, Input 11 High Safety Setpoint | N/A | N/A
49402:49403 | Term 3, Input 11 Low Safety Setpoint
49500:49501 | Term 3, Input 12 High Safety Setpoint | N/A | N/A
49502:49503 | Term 3, Input 12 Low Safety Setpoint
49600:49601 | Term 3, Input 13 High Safety Setpoint | N/A | N/A
49602:49603 | Term 3, Input 13 Low Safety Setpoint
49700:49701 | Term 3, Input 14 High Safety Setpoint | N/A | N/A
49702:49703 | Term 3, Input 14 Low Safety Setpoint
49800:49801 | Term 3, Input 15 High Safety Setpoint | N/A | N/A
49802:49803 | Term 3, Input 15 Low Safety Setpoint
49900:49901 | Term 3, Input 16 High Safety Setpoint | N/A | N/A
49902:49903 | Term 3, Input 16 Low Safety Setpoint
50000:50001 | Term 3, Input 17 High Safety Setpoint | N/A | N/A
50002:50003 | Term 3, Input 17 Low Safety Setpoint
50100:50101 | Term 3, Input 18 High Safety Setpoint | N/A | N/A
50102:50103 | Term 3, Input 18 Low Safety Setpoint
50200:50201 | Term 3, Input 19 High Safety Setpoint | N/A | N/A
50202:50203 | Term 3, Input 19 Low Safety Setpoint
50300:50301 | Term 3, Input 20 High Safety Setpoint | N/A | N/A
50302:50303 | Term 3, Input 20 Low Safety Setpoint
50400:50401 | Term 3, Input 21 High Safety Setpoint | N/A | N/A
50402:50403 | Term 3, Input 21 Low Safety Setpoint
50500:50501 | Term 3, Input 22 High Safety Setpoint | N/A | N/A
50502:50503 | Term 3, Input 22 Low Safety Setpoint
50600:50601 | Term 3, Input 23 High Safety Setpoint | N/A | N/A
50602:50603 | Term 3, Input 23 Low Safety Setpoint
50700:50701 | Term 3, Input 24 High Safety Setpoint | N/A | N/A
50702:50703 | Term 3, Input 24 Low Safety Setpoint
50800:50801 | Term 3, Input 25 High Safety Setpoint | N/A | N/A
50802:50803 | Term 3, Input 25 Low Safety Setpoint
50900:50901 | Term 3, Input 26 High Safety Setpoint | N/A | N/A
50902:50903 | Term 3, Input 26 Low Safety Setpoint
51000:51001 | Term 3, Input 27 High Safety Setpoint | N/A | N/A
51002:51003 | Term 3, Input 27 Low Safety Setpoint
51100:51101 | Term 3, Input 28 High Safety Setpoint | N/A | N/A
51102:51103 | Term 3, Input 28 Low Safety Setpoint
51200:51201 | Term 3, Input 29 High Safety Setpoint | N/A | N/A
51202:51203 | Term 3, Input 29 Low Safety Setpoint
51300:51301 | Term 3, Input 30 High Safety Setpoint | N/A | N/A
51302:51303 | Term 3, Input 30 Low Safety Setpoint
51400:51401 | Term 3, Input 31 High Safety Setpoint | N/A | N/A
51402:51403 | Term 3, Input 31 Low Safety Setpoint
51500:51501 | Term 3, Input 32 High Safety Setpoint | N/A | N/A
51502:51503 | Term 3, Input 32 Low Safety Setpoint
51600:51601 | Term 4, Input 1 High Safety Setpoint | N/A | N/A
51602:51603 | Term 4, Input 1 Low Safety Setpoint
51700:51701 | Term 4, Input 2 High Safety Setpoint | N/A | N/A
51702:51703 | Term 4, Input 2 Low Safety Setpoint
51800:51801 | Term 4, Input 3 High Safety Setpoint | N/A | N/A
51802:51803 | Term 4, Input 3 Low Safety Setpoint
51900:51901 | Term 4, Input 4 High Safety Setpoint | N/A | N/A
51902:51903 | Term 4, Input 4 Low Safety Setpoint
52000:52001 | Term 4, Input 5 High Safety Setpoint | N/A | N/A
52002:52003 | Term 4, Input 5 Low Safety Setpoint
52100:52101 | Term 4, Input 6 High Safety Setpoint | N/A | N/A
52102:52103 | Term 4, Input 6 Low Safety Setpoint
52200:52201 | Term 4, Input 7 High Safety Setpoint | N/A | N/A
52202:52203 | Term 4, Input 7 Low Safety Setpoint
52300:52301 | Term 4, Input 8 High Safety Setpoint | N/A | N/A
52302:52303 | Term 4, Input 8 Low Safety Setpoint
52400:52401 | Term 4, Input 9 High Safety Setpoint | N/A | N/A
52402:52403 | Term 4, Input 9 Low Safety Setpoint
52500:52501 | Term 4, Input 10 High Safety Setpoint | N/A | N/A
52502:52503 | Term 4, Input 10 Low Safety Setpoint
52600:52601 | Term 4, Input 11 High Safety Setpoint | N/A | N/A
52602:52603 | Term 4, Input 11 Low Safety Setpoint
52700:52701 | Term 4, Input 12 High Safety Setpoint | N/A | N/A
52702:52703 | Term 4, Input 12 Low Safety Setpoint
52800:52801 | Term 4, Input 13 High Safety Setpoint | N/A | N/A
52802:52803 | Term 4, Input 13 Low Safety Setpoint
52900:52901 | Term 4, Input 14 High Safety Setpoint | N/A | N/A
52902:52903 | Term 4, Input 14 Low Safety Setpoint
53000:53001 | Term 4, Input 15 High Safety Setpoint | N/A | N/A
53002:53003 | Term 4, Input 15 Low Safety Setpoint
53100:53101 | Term 4, Input 16 High Safety Setpoint | N/A | N/A
53102:53103 | Term 4, Input 16 Low Safety Setpoint
53200:53201 | Term 4, Input 17 High Safety Setpoint | N/A | N/A
53202:53203 | Term 4, Input 17 Low Safety Setpoint
53300:53301 | Term 4, Input 18 High Safety Setpoint | N/A | N/A
53302:53303 | Term 4, Input 18 Low Safety Setpoint
53400:53401 | Term 4, Input 19 High Safety Setpoint | N/A | N/A
53402:53403 | Term 4, Input 19 Low Safety Setpoint
53500:53501 | Term 4, Input 20 High Safety Setpoint | N/A | N/A
53502:53503 | Term 4, Input 20 Low Safety Setpoint
53600:53601 | Term 4, Input 21 High Safety Setpoint | N/A | N/A
53602:53603 | Term 4, Input 21 Low Safety Setpoint
53700:53701 | Term 4, Input 22 High Safety Setpoint | N/A | N/A
53702:53703 | Term 4, Input 22 Low Safety Setpoint
53800:53801 | Term 4, Input 23 High Safety Setpoint | N/A | N/A
53802:53803 | Term 4, Input 23 Low Safety Setpoint
53900:53901 | Term 4, Input 24 High Safety Setpoint | N/A | N/A
53902:53903 | Term 4, Input 24 Low Safety Setpoint
54000:54001 | Term 4, Input 25 High Safety Setpoint | N/A | N/A
54002:54003 | Term 4, Input 25 Low Safety Setpoint
54100:54101 | Term 4, Input 26 High Safety Setpoint | N/A | N/A
54102:54103 | Term 4, Input 26 Low Safety Setpoint
54200:54201 | Term 4, Input 27 High Safety Setpoint | N/A | N/A
54202:54203 | Term 4, Input 27 Low Safety Setpoint
54300:54301 | Term 4, Input 28 High Safety Setpoint | N/A | N/A
54302:54303 | Term 4, Input 28 Low Safety Setpoint
54400:54401 | Term 4, Input 29 High Safety Setpoint | N/A | N/A
54402:54403 | Term 4, Input 29 Low Safety Setpoint
54500:54501 | Term 4, Input 30 High Safety Setpoint | N/A | N/A
54502:54503 | Term 4, Input 30 Low Safety Setpoint
54600:54601 | Term 4, Input 31 High Safety Setpoint | N/A | N/A
54602:54603 | Term 4, Input 31 Low Safety Setpoint
54700:54701 | Term 4, Input 32 High Safety Setpoint | N/A | N/A
54702:54703 | Term 4, Input 32 Low Safety Setpoint
54800:54801 | Term 5, Input 1 High Safety Setpoint | N/A | N/A
54802:54803 | Term 5, Input 1 Low Safety Setpoint
54900:54901 | Term 5, Input 2 High Safety Setpoint | N/A | N/A
54902:54903 | Term 5, Input 2 Low Safety Setpoint
55000:55001 | Term 5, Input 3 High Safety Setpoint | N/A | N/A
55002:55003 | Term 5, Input 3 Low Safety Setpoint
55100:55101 | Term 5, Input 4 High Safety Setpoint | N/A | N/A
55102:55103 | Term 5, Input 4 Low Safety Setpoint
55200:55201 | Term 5, Input 5 High Safety Setpoint | N/A | N/A
55202:55203 | Term 5, Input 5 Low Safety Setpoint
55300:55301 | Term 5, Input 6 High Safety Setpoint | N/A | N/A
55302:55303 | Term 5, Input 6 Low Safety Setpoint
55400:55401 | Term 5, Input 7 High Safety Setpoint | N/A | N/A
55402:55403 | Term 5, Input 7 Low Safety Setpoint
55500:55501 | Term 5, Input 8 High Safety Setpoint | N/A | N/A
55502:55503 | Term 5, Input 8 Low Safety Setpoint
55600:55601 | Term 5, Input 9 High Safety Setpoint | N/A | N/A
55602:55603 | Term 5, Input 9 Low Safety Setpoint
55700:55701 | Term 5, Input 10 High Safety Setpoint | N/A | N/A
55702:55703 | Term 5, Input 10 Low Safety Setpoint
55800:55801 | Term 5, Input 11 High Safety Setpoint | N/A | N/A
55802:55803 | Term 5, Input 11 Low Safety Setpoint
55900:55901 | Term 5, Input 12 High Safety Setpoint | N/A | N/A
55902:55903 | Term 5, Input 12 Low Safety Setpoint
56000:56001 | Term 5, Input 13 High Safety Setpoint | N/A | N/A
56002:56003 | Term 5, Input 13 Low Safety Setpoint
56100:56101 | Term 5, Input 14 High Safety Setpoint | N/A | N/A
56102:56103 | Term 5, Input 14 Low Safety Setpoint
56200:56201 | Term 5, Input 15 High Safety Setpoint | N/A | N/A
56202:56203 | Term 5, Input 15 Low Safety Setpoint
56300:56301 | Term 5, Input 16 High Safety Setpoint | N/A | N/A
56302:56303 | Term 5, Input 16 Low Safety Setpoint
56400:56401 | Term 5, Input 17 High Safety Setpoint | N/A | N/A
56402:56403 | Term 5, Input 17 Low Safety Setpoint
56500:56501 | Term 5, Input 18 High Safety Setpoint | N/A | N/A
56502:56503 | Term 5, Input 18 Low Safety Setpoint
56600:56601 | Term 5, Input 19 High Safety Setpoint | N/A | N/A
56602:56603 | Term 5, Input 19 Low Safety Setpoint
56700:56701 | Term 5, Input 20 High Safety Setpoint | N/A | N/A
56702:56703 | Term 5, Input 20 Low Safety Setpoint
56800:56801 | Term 5, Input 21 High Safety Setpoint | N/A | N/A
56802:56803 | Term 5, Input 21 Low Safety Setpoint
56900:56901 | Term 5, Input 22 High Safety Setpoint | N/A | N/A
56902:56903 | Term 5, Input 22 Low Safety Setpoint
57000:57001 | Term 5, Input 23 High Safety Setpoint | N/A | N/A
57002:57003 | Term 5, Input 23 Low Safety Setpoint
57100:57101 | Term 5, Input 24 High Safety Setpoint | N/A | N/A
57102:57103 | Term 5, Input 24 Low Safety Setpoint
57200:57201 | Term 5, Input 25 High Safety Setpoint | N/A | N/A
57202:57203 | Term 5, Input 25 Low Safety Setpoint
57300:57301 | Term 5, Input 26 High Safety Setpoint | N/A | N/A
57302:57303 | Term 5, Input 26 Low Safety Setpoint
57400:57401 | Term 5, Input 27 High Safety Setpoint | N/A | N/A
57402:57403 | Term 5, Input 27 Low Safety Setpoint
57500:57501 | Term 5, Input 28 High Safety Setpoint | N/A | N/A
57502:57503 | Term 5, Input 28 Low Safety Setpoint
57600:57601 | Term 5, Input 29 High Safety Setpoint | N/A | N/A
57602:57603 | Term 5, Input 29 Low Safety Setpoint
57700:57701 | Term 5, Input 30 High Safety Setpoint | N/A | N/A
57702:57703 | Term 5, Input 30 Low Safety Setpoint
57800:57801 | Term 5, Input 31 High Safety Setpoint | N/A | N/A
57802:57803 | Term 5, Input 31 Low Safety Setpoint
57900:57901 | Term 5, Input 32 High Safety Setpoint | N/A | N/A
57902:57903 | Term 5, Input 32 Low Safety Setpoint